## SelectionData
Selection Table SLS / SLB / SLF
flow rate, Q | [m³/h] | 300
diffuser length, L | [mm] | 1000
throw, LT | [m] | 4
supply temperature, Ts | [°C] | 18
room temperature, Tr | [°C] | 26
room attenuation | [NR] | 8
acoustics unit |  | NR
| Type | SLS-1 SLB-1 | SLS-2 SLB-2 SLF-2 | SLS-3 SLB-3 SLF-3 | SLS-4 SLB-4 SLF-4
| L [mm] | 1000 | 1000 | 1000 | 1000
Airflow direction
| Damper position | 100% (open) | 100% (open) | 100% (open) | 100% (open)
| Plenum | SP--1 | SP--2 | SP--3 | SP--4
effective air velocity, Veff | [m/s] | 5.4707 | 3.3951 | 2.4613 | 1.9303 | 8.504 | 4.3205 | 2.8841 | 2.1621
static pressure, DPs | [Pa] | 57.2304 | 11.5407 | 6.2865 | 3.5855
total pressure, DPtot | [Pa] | 84.8979 | 21.8476 | 10.5082 | 7.8072
throw velocity, vT @ LT | [m/s] | 0.4234 | 0.36218 | 0.3336 | 0.31854
critical distance | [m] | 12.3751 | 5.8223 | 3.7458 | 2.7393
air temperature @ LT | [°C] | 25.7373 | 25.563 | 25.3635 | 25.1416
sound power, Lw | [NR] | >50 | 30.1105 | 24.1036 | 18.1455
sound pressure, Lp | [NR] | 47.1727 | 22.1105 | 16.1036 | <15
Sound Spectrum
|  | Lw [dB] |  |  |  | Lw [dB]
125 | [Hz] | 58.3533 | 42.7833 | 40.7657 | 33.762
250 | [Hz] | 58.0443 | 40.0028 | 34.4163 | 28.8753
500 | [Hz] | 58.5382 | 32.6599 | 24.6533 | 17.365
1000 | [Hz] | 52.9177 | 26.6546 | 17.869 | 8.8784
2000 | [Hz] | 47.2824 | 15.2573 | 5.1685 | < BGL
4000 | [Hz] | 39.2532 | 5.7891 | < BGL | < BGL
8000 | [Hz] | < BGL | < BGL | < BGL | < BGL
< BGL : Lw below background level

## units (hidden)
dB(A)
NR

## TechData (hidden)
|  |  | HORIZONTAL FLOW |  |  |  | VERTICAL FLOW
|  | Type | SLS-1 SLB-1 | SLS-2 SLB-2 SLF-2 | SLS-3 SLB-3 SLF-3 | SLS-4 SLB-4 SLF-4 | SLS-1 SLB-1 | SLS-2 SLB-2 | SLS-3 SLB-3 SLF-3 | SLS-4 SLB-4 SLF-4
|  | Size | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000
|  | condition 1 | deflectors in/out | deflectors in/out | deflectors in/out | deflectors in/out | deflectors out/out | deflectors out/out | deflectors out/out | deflectors out/out
|  | condition 2 | 100% (open) | 100% (open) | 100% (open) | 100% (open) | 100% (open) | 100% (open) | 100% (open) | 100% (open)
|  | condition 3 | SP--1 | SP--2 | SP--3 | SP--4 | SP--1 | SP--2 | SP--3 | SP--4
THROW
|  | Ak [m²] | 0.015233 | 0.024545 | 0.033858 | 0.04317 | 0.0097993 | 0.019288 | 0.028894 | 0.038543
|  | K1 [m] | 2.9898 | 3.1928 | 3.3958 | 3.5987 | 4.5105 | 3.3546 | 2.1577 | 0.92533
|  | X0 [m] | -0.76792 | -0.68901 | -0.6101 | -0.53119 | -2.0316 | -1.5087 | -0.97578 | -0.4275
PRESSURE LOSS
|  | A | 39.8239 | 88.1777 | 118.3174 | 159.1897 | 32.7402 | 63.8522 | 100.2806 | 124.032
|  | B | 0.49896 | 0.50061 | 0.5061 | 0.49627 | 0.48846 | 0.51743 | 0.48674 | 0.50965
|  | Aduct [m²] | 0.012272 | 0.020106 | 0.031416 | 0.031416 | 0.012272 | 0.020106 | 0.031416 | 0.031416
CRITICAL DISTANCE (function of DT)
| at 4°C | A | 1.387 | 1.387 | 1.387 | 1.387
|  | B | -2.1599 | -2.4874 | -2.6789 | -2.8148
| at 6°C | A | 1.387 | 1.387 | 1.387 | 1.387
|  | B | -2.2672 | -2.5946 | -2.7862 | -2.9221
| at 8°C | A | 1.387 | 1.387 | 1.387 | 1.387
|  | B | -2.3433 | -2.6707 | -2.8623 | -2.9982
| at 10°C | A | 1.387 | 1.387 | 1.387 | 1.387
|  | B | -2.4023 | -2.7298 | -2.9213 | -3.0572
| at 12°C | A | 1.387 | 1.387 | 1.387 | 1.387
|  | B | -2.4505 | -2.778 | -2.9695 | -3.1054
TEMPERATURE
|  | Ak [m²] | 0.01403 | 0.02181 | 0.02959 | 0.03737
|  | K2 [-] | 1.1368 | 1.517 | 1.8973 | 2.2775
|  | X0 [m] | -0.099822 | -0.10102 | -0.10222 | -0.10341
SOUND POWER, NR
|  | A | 31.5349 | 30.2937 | 31.7033 | 32.6709
|  | B | -124.6955 | -142.6781 | -156.725 | -168.2022
SOUND POWER, dB(A)
|  | A | 28.8317 | 29.7404 | 28.8954 | 31.031
|  | B | -107.4515 | -134.2798 | -135.2064 | -154.037
SOUND POWER SPECTRUM
| at 125 Hz | A | 22.5623 | 21.1999 | 22.3969 | 25.4369
|  | B | -70.3371 | -78.1363 | -86.9812 | -111.3244
| at 250 Hz | A | 25.9845 | 28.1731 | 29.484 | 30.3839
|  | B | -90.1659 | -120.6906 | -133.7542 | -144.428
| at 500 Hz | A | 30.715 | 32.8446 | 32.0228 | 33.6826
|  | B | -116.6534 | -154.6788 | -157.9978 | -174.7532
| at 1 kHz | A | 37.8021 | 38.8025 | 38.3526 | 41.3305
|  | B | -162.6972 | -194.6662 | -200.8858 | -226.862
| at 2 kHz | A | 43.2873 | 47.3986 | 46.488 | 44.8024
|  | B | -199.6188 | -255.0938 | -259.9889 | -257.3935
| at 4 kHz | A | 46.4959 | 44.7859 | 54.4997 | 70.436
|  | B | -225.9494 | -249.6598 | -320.6496 | -430.4359
| at 8 kHz | A
B
END

## IntermediateCalcul (hidden)
Critical distance
Type | SLS-1 SLB-1 | SLS-2 SLB-2 SLF-2 | SLS-3 SLB-3 SLF-3 | SLS-4 SLB-4 SLF-4 | #REF! | #REF! | SLS-1 SLB-1 | SLS-2 SLB-2 | SLS-3 SLB-3 SLF-3
Size | 1000 | 1000 | 1000 | 1000 | #REF! | #REF! | 1000 | 1000 | 1000
condition 1 | deflectors in/out | deflectors in/out | deflectors in/out | deflectors in/out | #REF! | #REF! | deflectors out/out | deflectors out/out | deflectors out/out
condition 2 | 100% (open) | 100% (open) | 100% (open) | 100% (open) | #REF! | #REF! | 100% (open) | 100% (open) | 100% (open)
condition 3 | SP--1 | SP--2 | SP--3 | SP--4 | #REF! | #REF! | SP--1 | SP--2 | SP--3
A
dT
4 | 1.387 | 1.387 | 1.387 | 1.387 | #REF! | #REF!
6 | 1.387 | 1.387 | 1.387 | 1.387 | #REF! | #REF!
8 | 1.387 | 1.387 | 1.387 | 1.387 | #REF! | #REF!
10 | 1.387 | 1.387 | 1.387 | 1.387 | #REF! | #REF!
12 | 1.387 | 1.387 | 1.387 | 1.387 | #REF! | #REF!
B
4 | -2.1599 | -2.4874 | -2.6789 | -2.8148 | #REF! | #REF!
6 | -2.2672 | -2.5946 | -2.7862 | -2.9221 | #REF! | #REF!
8 | -2.3433 | -2.6707 | -2.8623 | -2.9982 | #REF! | #REF!
10 | -2.4023 | -2.7298 | -2.9213 | -3.0572 | #REF! | #REF!
12 | -2.4505 | -2.778 | -2.9695 | -3.1054 | #REF! | #REF!
dT requested
8
dT1 | 8 | 8 | 8 | 8 | #REF! | #REF!
dT2 | 10 | 10 | 10 | 10 | #REF! | #REF!
A1 | 1.387 | 1.387 | 1.387 | 1.387 | #REF! | #REF!
A2 | 1.387 | 1.387 | 1.387 | 1.387 | #REF! | #REF!
B1 | -2.3433 | -2.6707 | -2.8623 | -2.9982 | #REF! | #REF!
B2 | -2.4023 | -2.7298 | -2.9213 | -3.0572 | #REF! | #REF!

## CorrectionFactors (hidden)
Noise correction - diffuser length
cNR | -3.0985e-05
Throw correction - diffuser length
cK1 | 1