## SelectionData
Selection Table RT
flow rate, Q | [m³/h] | 120
diffuser length, L | [mm] | 1000
throw, LT | [m] | 4
supply temperature, Ts | [°C] | 24
room temperature, Tr | [°C] | 26
room attenuation | [NR] | 8
acoustics unit |  | NR
| Type | RT1 | RT2 | RT3 | RT4 | RT5 | RT6
| L [mm] | 1000 | 1000 | 1000 | 1000 | 1000 | 1000
Airflow direction
| Damper position | 100% (open) | 100% (open) | 100% (open) | 100% (open) | 100% (open) | 100% (open)
| Plenum | RP--1 | RP--2 | RP--3 | RP--4 | RP--5 | RP--6
effective air velocity, Veff | [m/s] | 3.009 | 1.8647 | 1.351 | 1.0592 | 0.87104 | 0.73966
static pressure, DPs | [Pa] | 16.9851 | 4.929 | 2.3177 | 1.3446 | <1 | <1
total pressure, DPtot | [Pa] | 21.4119 | 6.5781 | 2.9932 | 2.0201 | 1.1546 | <1
throw velocity, vT @ LT | [m/s] | 0.51152 | 0.38721 | 0.31502 | 0.2646 | 0.22542 | 0.19265
critical distance | [m] | 5.0588 | 3.023 | 2.2369 | 1.8065 | 1.5305 | 1.3367
air temperature @ LT | [°C] | bar: RP--1 to RP--6
sound power, Lw | [NR] | 30.4024 | 15.2939 | <15 | <15 | <15 | <15
sound pressure, Lp | [NR] | 22.4024 | <15 | <15 | <15 | <15 | <15
Sound Spectrum
Lw [dB]
125 | [Hz] | 38.8587 | 30.1071 | - | - | - | -
250 | [Hz] | 40.2742 | 26.2234 | - | - | - | -
500 | [Hz] | 31.5493 | 15.6386 | - | - | - | -
1000 | [Hz] | 25.6003 | 6.7745 | - | - | - | -
2000 | [Hz] | 17.9824 | < BGL | - | - | - | -
4000 | [Hz] | 8.9651 | < BGL | - | - | - | -
8000 | [Hz] | < BGL | < BGL | - | - | - | -
< BGL : Lw below background level

## units (hidden)
dB(A)
NR

## TechData (hidden)
HORIZONTAL FLOW
|  | Type | RT1 | RT2 | RT3 | RT4 | RT5 | RT6
|  | Size | 1000 | 1000 | 1000 | 1000 | 1000 | 1000
condition 1
|  | condition 2 | 100% (open) | 100% (open) | 100% (open) | 100% (open) | 100% (open) | 100% (open)
|  | condition 3 | RP--1 | RP--2 | RP--3 | RP--4 | RP--5 | RP--6
THROW
|  | Ak [m²] | 0.011078 | 0.017876 | 0.024673 | 0.031471 | 0.038268 | 0.045066
|  | K1 [m] | 12.3234 | 11.2838 | 10.2441 | 9.2045 | 8.1648 | 7.1252
|  | X0 [m] | -3.6299 | -3.2654 | -2.9009 | -2.5364 | -2.1719 | -1.8075
PRESSURE LOSS
|  | A | 28.5603 | 53.4664 | 78.3725 | 103.2786 | 128.1847 | 153.0908
|  | B | 0.50682 | 0.50682 | 0.50682 | 0.50682 | 0.50682 | 0.50682
|  | Aduct [m²] | 0.012272 | 0.020106 | 0.031416 | 0.031416 | 0.049087 | 0.049087
CRITICAL DISTANCE (function of DT)
| at 4°C | A | 0.8079 | 0.8079 | 0.8079 | 0.8079 | 0.8079 | 0.8079
|  | B | -1.0164 | -1.24 | -1.3708 | -1.4636 | -1.5356 | -1.5944
| at 6°C | A | 0.8079 | 0.8079 | 0.8079 | 0.8079 | 0.8079 | 0.8079
|  | B | -1.0571 | -1.2807 | -1.4115 | -1.5043 | -1.5763 | -1.6351
| at 8°C | A | 0.8079 | 0.8079 | 0.8079 | 0.8079 | 0.8079 | 0.8079
|  | B | -1.086 | -1.3096 | -1.4404 | -1.5332 | -1.6052 | -1.664
| at 10°C | A | 0.8079 | 0.8079 | 0.8079 | 0.8079 | 0.8079 | 0.8079
|  | B | -1.1083 | -1.332 | -1.4628 | -1.5556 | -1.6276 | -1.6864
| at 12°C | A | 0.8079 | 0.8079 | 0.8079 | 0.8079 | 0.8079 | 0.8079
|  | B | -1.1266 | -1.3503 | -1.4811 | -1.5739 | -1.6458 | -1.7047
TEMPERATURE
Ak [m²]
K2 [-]
X0 [m]
SOUND POWER, NR
|  | A | 28.5536 | 28.5719 | 28.5628 | 28.6062 | 28.5693 | 28.5972
|  | B | -106.2979 | -121.494 | -131.6889 | -136.7736 | -144.0501 | -147.352
SOUND POWER, dB(A)
|  | A | 28.1058 | 28.0368 | 28.0669 | 27.8364 | 27.9981 | 27.8208
|  | B | -99.8952 | -114.0723 | -124.0389 | -127.2967 | -135.3567 | -137.2137
SOUND POWER SPECTRUM
| at 125 Hz | A | 19.7126 | 19.7252 | 19.7189 | 19.7488 | 19.7233 | 19.7426
|  | B | -55.5153 | -64.327 | -70.3832 | -73.1968 | -77.6799 | -79.5178
| at 250 Hz | A | 26.5549 | 26.5719 | 26.5634 | 26.6038 | 26.5694 | 26.5954
|  | B | -86.857 | -100.9894 | -110.4707 | -115.1995 | -121.9666 | -125.0373
| at 500 Hz | A | 29.6258 | 29.6448 | 29.6354 | 29.6804 | 29.6421 | 29.671
|  | B | -110.284 | -126.2856 | -137.0007 | -142.3738 | -149.9992 | -153.4868
| at 1 kHz | A | 37.5425 | 37.5666 | 37.5546 | 37.6116 | 37.5631 | 37.5997
|  | B | -154.1342 | -173.0751 | -185.8717 | -192.126 | -201.3587 | -205.4267
| at 2 kHz | A | 46.1743 | 46.2039 | 46.1891 | 46.2593 | 46.1996 | 46.2446
|  | B | -203.0764 | -225.8297 | -241.251 | -248.718 | -259.8988 | -264.7594
| at 4 kHz | A | 44.9453 | 44.9739 | 44.9596 | 45.0276 | 44.9698 | 45.0134
|  | B | -206.2099 | -229.5463 | -245.2528 | -253.0132 | -264.2809 | -269.3232
| at 8 kHz | A | RP--4: 44.9373; RP--5: 44.8791; RP--6: 44.923
|  | B | RP--4: -267.9883; RP--5: -279.5091; RP--6: -284.7714
END

## IntermediateCalcul (hidden)
Critical distance
Type | RT1 | RT2 | RT3 | RT4 | RT5 | RT6 | #REF! | #REF! | #REF!
Size | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | #REF! | #REF! | #REF!
condition 1 | [6 empty] | #REF! | #REF! | #REF!
condition 2 | 100% (open) | 100% (open) | 100% (open) | 100% (open) | 100% (open) | 100% (open) | #REF! | #REF! | #REF!
condition 3 | RP--1 | RP--2 | RP--3 | RP--4 | RP--5 | RP--6 | #REF! | #REF! | #REF!
A
dT
4 | 0.8079 | 0.8079 | 0.8079 | 0.8079 | 0.8079 | 0.8079 | #REF! | #REF! | #REF!
6 | 0.8079 | 0.8079 | 0.8079 | 0.8079 | 0.8079 | 0.8079 | #REF! | #REF! | #REF!
8 | 0.8079 | 0.8079 | 0.8079 | 0.8079 | 0.8079 | 0.8079 | #REF! | #REF! | #REF!
10 | 0.8079 | 0.8079 | 0.8079 | 0.8079 | 0.8079 | 0.8079 | #REF! | #REF! | #REF!
12 | 0.8079 | 0.8079 | 0.8079 | 0.8079 | 0.8079 | 0.8079 | #REF! | #REF! | #REF!
B
4 | -1.0164 | -1.24 | -1.3708 | -1.4636 | -1.5356 | -1.5944 | #REF! | #REF! | #REF!
6 | -1.0571 | -1.2807 | -1.4115 | -1.5043 | -1.5763 | -1.6351 | #REF! | #REF! | #REF!
8 | -1.086 | -1.3096 | -1.4404 | -1.5332 | -1.6052 | -1.664 | #REF! | #REF! | #REF!
10 | -1.1083 | -1.332 | -1.4628 | -1.5556 | -1.6276 | -1.6864 | #REF! | #REF! | #REF!
12 | -1.1266 | -1.3503 | -1.4811 | -1.5739 | -1.6458 | -1.7047 | #REF! | #REF! | #REF!
dT requested
2
dT1 | 4 | 4 | 4 | 4 | 4 | 4 | #REF! | #REF! | #REF!
dT2 | 6 | 6 | 6 | 6 | 6 | 6 | #REF! | #REF! | #REF!
A1 | 0.8079 | 0.8079 | 0.8079 | 0.8079 | 0.8079 | 0.8079 | #REF! | #REF! | #REF!
A2 | 0.8079 | 0.8079 | 0.8079 | 0.8079 | 0.8079 | 0.8079 | #REF! | #REF! | #REF!
B1 | -1.0164 | -1.24 | -1.3708 | -1.4636 | -1.5356 | -1.5944 | #REF! | #REF! | #REF!
B2 | -1.0571 | -1.2807 | -1.4115 | -1.5043 | -1.5763 | -1.6351 | #REF! | #REF! | #REF!

## CorrectionFactors (hidden)
Noise correction - diffuser length
cNR | -3.0985e-05
Throw correction - diffuser length
cK1 | 1