## SelectionData
Selection Table
flow rate, Q | [m³/h] | 50
throw, LT | [m] | 1.8
supply temperature, Ts | [°C] | 15
room temperature, Tr | [°C] | 20
room attenuation | [dB(A)] | 8
acoustics unit |  | dB(A)
| Type | VMH011 | VMH011 | VMH011 | VMH011 | VMH011 | VMH011
| Size | 150 | 150 | 150 | 200 | 200 | 200
| condition 1 | damper 25% | damper 50% | damper 100% | damper 25% | damper 50% | damper 100%
condition 2
condition 3
effective air velocity, Veff | [m/s] | 2.4442 | 2.4442 | 2.4442 | 1.3409 | 1.3409 | 1.3409
static pressure, DPs | [Pa] | 96.9627 | 76.1809 | 56.9148 | 22.9654 | 15.7466 | 13.1224
total pressure, DPtot | [Pa] | 97.3333 | 76.5515 | 57.2854 | 23.0827 | 15.8638 | 13.2397
throw velocity, vT @ LT | [m/s] | 0.24181 | 0.24181 | 0.24181 | 0.18028 | 0.18028 | 0.18028
critical distance | [m] | - | - | - | - | - | -
air temperature @ LT | [°C] | 19.7023 | 19.7023 | 19.7023 | 19.8012 | 19.8012 | 19.8012
sound power, Lw | [dB(A)] | 46.3325 | 46.3882 | 43.1279 | 31.6344 | 28.1748 | 25.6267
sound pressure, Lp | [dB(A)] | 38.3325 | 38.3882 | 35.1279 | 23.6344 | 20.1748 | <20
Sound Spectrum
Lw [dB]
125 | [Hz] | 48.008 | 49.7776 | 47.299 | 41.0444 | 38.9963 | 38.4006
250 | [Hz] | 44.9111 | 47.6246 | 44.9812 | 34.9155 | 31.9197 | 28.6748
500 | [Hz] | 41.7593 | 42.6509 | 39.9361 | 26.9315 | 22.8996 | 19.7151
1000 | [Hz] | 44.1314 | 44.4705 | 39.5137 | 24.5891 | 19.5937 | 15.1209
2000 | [Hz] | 41.8289 | 42.8394 | 34.6428 | 12.9082 | 5.8304 | 0.61055
4000 | [Hz] | 31.4512 | 31.1698 | 27.2806 | 0.42971 | < BGL | < BGL
8000 | [Hz] | < BGL | < BGL | < BGL | < BGL | < BGL | < BGL
< BGL : Lw below background level

## units (hidden)
dB(A)
NR

## TechData (hidden)
|  | Type | VMH011 | VMH011 | VMH011 | VMH011 | VMH011 | VMH011
|  | Size | 150 | 150 | 150 | 200 | 200 | 200
|  | condition 1 | damper 25% | damper 50% | damper 100% | damper 25% | damper 50% | damper 100%
condition 2
condition 3
THROW
|  | Ak [m²] | 0.0056825 | 0.0056825 | 0.0056825 | 0.010358 | 0.010358 | 0.010358
|  | K1 [m] | 2.8045 | 2.8045 | 2.8045 | 2.8045 | 2.8045 | 2.8045
|  | X0 [m] | -0.33691 | -0.33691 | -0.33691 | -0.32295 | -0.32295 | -0.32295
PRESSURE LOSS
|  | A | 3.9085 | 5.1288 | 6.218 | 9.5966 | 11.8832 | 12.8307
|  | B | 0.55721 | 0.52552 | 0.51579 | 0.52668 | 0.52125 | 0.52836
|  | Aduct [m²] | 0.017671 | 0.017671 | 0.017671 | 0.031416 | 0.031416 | 0.031416
CRITICAL DISTANCE (function of DT)
| at 4°C | A
B
| at 6°C | A
B
| at 8°C | A
B
| at 10°C | A
B
| at 12°C | A
B
TEMPERATURE
|  | Ak [m²] | 0.0056825 | 0.0056825 | 0.0056825 | 0.010358 | 0.010358 | 0.010358
|  | K2 [-] | 1.4183 | 1.4183 | 1.4183 | 0.68715 | 0.68715 | 0.68715
|  | X0 [m] | 0.0044627 | 0.0044627 | 0.0044627 | 0.040958 | 0.040958 | 0.040958
SOUND POWER, NR
|  | A | 29.9123 | 28.437 | 26.8407 | 30.6064 | 30.4846 | 29.016
|  | B | -73.3384 | -69.3758 | -66.5877 | -93.4794 | -97.2495 | -94.3344
SOUND POWER, dB(A)
|  | A | 24.8976 | 25.9663 | 24.7124 | 26.6822 | 26.3425 | 26.3973
|  | B | -51.0676 | -55.1925 | -53.5477 | -72.7468 | -74.8778 | -77.6403
SOUND POWER SPECTRUM
| at 125 Hz | A | 13.2286 | 14.7305 | 14.8197 | 18.7134 | 16.3997 | 16.4528
|  | B | -3.7424 | -7.8486 | -10.676 | -32.1626 | -25.1598 | -25.963
| at 250 Hz | A | 19.3797 | 22.9568 | 21.0192 | 22.0925 | 22.4925 | 24.7224
|  | B | -30.9028 | -42.1829 | -37.2463 | -51.5107 | -56.0716 | -68.0399
| at 500 Hz | A | 25.2996 | 28.4614 | 26.7399 | 26.6924 | 26.1258 | 27.311
|  | B | -57.2132 | -68.6907 | -64.6712 | -77.4898 | -79.3052 | -87.1263
| at 1 kHz | A | 31.1847 | 38.0047 | 34.9837 | 37.4249 | 36.7373 | 37.0063
|  | B | -77.8637 | -104.2048 | -97.3434 | -121.818 | -124.1236 | -129.6487
| at 2 kHz | A | 38.2531 | 47.1751 | 40.849 | 49.8808 | 53.9131 | 55.3936
|  | B | -107.8181 | -141.7107 | -125.1595 | -182.2265 | -205.0789 | -216.0906
| at 4 kHz | A | 45.1663 | 46.267 | 48.2354 | 50.4493 | 47.6213 | 50.6994
|  | B | -145.2403 | -149.8279 | -161.4173 | -196.9292 | -188.8589 | -205.4093
| at 8 kHz | A
B
END

## IntermediateCalcul (hidden)
Critical distance
Type | VMH011 | VMH011 | VMH011 | VMH011 | VMH011 | VMH011
Size | 150 | 150 | 150 | 200 | 200 | 200
condition 1 | damper 25% | damper 50% | damper 100% | damper 25% | damper 50% | damper 100%
condition 2
condition 3
A
dT
4
6
8
10
12
B
4
6
8
10
12
dT requested
5
dT1
dT2
A1
A2
B1
B2