## SelectionData
Selection Table
flow rate, Q | [m³/h] | 50
throw, LT | [m] | 1
supply temperature, Ts | [°C] | 15
room temperature, Tr | [°C] | 20
room attenuation | [dB(A)] | 8
acoustics unit |  | dB(A)
| Type | VMV011 | VMV011 | VMV011 | VMV011 | VMV011 | VMV011
| Size | 150 | 150 | 150 | 200 | 200 | 200
| condition 1 | damper 25% | damper 50% | damper 100% | damper 25% | damper 50% | damper 100%
condition 2
condition 3
effective air velocity, Veff | [m/s] | 6.8565 | 6.8565 | 6.8565 | 3.0661 | 3.0661 | 3.0661
static pressure, DPs | [Pa] | 75.8807 | 53.5961 | 43.5339 | 17.2578 | 12.4724 | 9.6942
total pressure, DPtot | [Pa] | 76.2513 | 53.9668 | 43.9046 | 17.3751 | 12.5896 | 9.8115
throw velocity, vT @ LT | [m/s] | 0.27881 | 0.27881 | 0.27881 | 0.2088 | 0.2088 | 0.2088
critical distance | [m] | - | - | - | - | - | -
air temperature @ LT | [°C] | - | - | - | - | - | -
sound power, Lw | [dB(A)] | 45.1879 | 42.7494 | 39.4307 | 27.3196 | 25.3763 | 22.2588
sound pressure, Lp | [dB(A)] | 37.1879 | 34.7494 | 31.4307 | <20 | <20 | <20
Sound Spectrum
Lw [dB]
125 | [Hz] | 47.4401 | 47.7969 | 46.2143 | 38.1217 | 36.6793 | 33.5748
250 | [Hz] | 44.8763 | 45.3781 | 41.8708 | 31.6541 | 30.4036 | 27.9322
500 | [Hz] | 40.8879 | 39.5507 | 36.239 | 22.7412 | 20.2308 | 17.4189
1000 | [Hz] | 43.1395 | 38.9723 | 33.9505 | 16.7669 | 12.9399 | 8.9343
2000 | [Hz] | 40.1368 | 33.6546 | 27.1504 | 4.714 | 0.00021371 | < BGL
4000 | [Hz] | 30.8467 | 24.8078 | 19.0265 | < BGL | < BGL | < BGL
8000 | [Hz] | < BGL | < BGL | < BGL | < BGL | < BGL | < BGL
< BGL : Lw below background level

## TechData (hidden)
|  | Type | VMV011 | VMV011 | VMV011 | VMV011 | VMV011 | VMV011
|  | Size | 150 | 150 | 150 | 200 | 200 | 200
|  | condition 1 | damper 25% | damper 50% | damper 100% | damper 25% | damper 50% | damper 100%
condition 2
condition 3
THROW
|  | Ak [m²] | 0.0020256 | 0.0020256 | 0.0020256 | 0.0045298 | 0.0045298 | 0.0045298
|  | K1 [m] | 0.78011 | 0.78011 | 0.78011 | 0.78011 | 0.78011 | 0.78011
|  | X0 [m] | 0.13656 | 0.13656 | 0.13656 | 0.22902 | 0.22902 | 0.22902
PRESSURE LOSS
|  | A | 4.6704 | 6.2167 | 7.0689 | 11.493 | 13.2334 | 15.3307
|  | B | 0.54763 | 0.52362 | 0.51843 | 0.5162 | 0.52676 | 0.52043
|  | Aduct [m²] | 0.017671 | 0.017671 | 0.017671 | 0.031416 | 0.031416 | 0.031416
CRITICAL DISTANCE (function of DT)
| at 4°C | A
B
| at 6°C | A
B
| at 8°C | A
B
| at 10°C | A
B
| at 12°C | A
B
TEMPERATURE
Ak [m²]
K2 [-]
X0 [m]
SOUND POWER, NR
|  | A | 26.9571 | 24.8174 | 25.2329 | 27.848 | 24.653 | 25.1475
|  | B | -63.7346 | -59.1283 | -64.5263 | -87.4758 | -76.7315 | -81.6261
SOUND POWER, dB(A)
|  | A | 23.1744 | 22.847 | 22.7975 | 25.3939 | 23.3947 | 24.4396
|  | B | -45.4708 | -46.6287 | -49.7537 | -72.0218 | -66.1445 | -73.3493
SOUND POWER SPECTRUM
| at 125 Hz | A | 12.7999 | 13.4276 | 14.3191 | 18.2311 | 17.0213 | 18.4199
|  | B | -2.6334 | -4.7321 | -9.8024 | -33.1989 | -29.9085 | -38.4841
| at 250 Hz | A | 18.2494 | 20.3709 | 20.0724 | 21.2339 | 20.5873 | 20.9919
|  | B | -26.5156 | -34.3133 | -36.6528 | -51.4135 | -50.1343 | -54.1888
| at 500 Hz | A | 22.7136 | 26.1517 | 24.6641 | 26.6886 | 25.2898 | 26.3071
|  | B | -47.9682 | -62.7552 | -60.2473 | -81.6652 | -78.7034 | -85.4951
| at 1 kHz | A | 31.615 | 35.4302 | 33.2037 | 37.7505 | 34.9462 | 35.4169
|  | B | -80.5392 | -99.6316 | -95.9432 | -130.9139 | -123.7704 | -129.6176
| at 2 kHz | A | 39.0044 | 42.8483 | 40.7257 | 45.8309 | 42.0249 | 41.8549
|  | B | -112.4493 | -133.9689 | -132.1695 | -174.5777 | -164.4021 | -167.8803
| at 4 kHz | A | 40.2495 | 45.3274 | 45.27 | 48.5733 | 46.2068 | 47.1877
|  | B | -126.6104 | -152.5142 | -158.0708 | -195.2558 | -191.1315 | -198.8412
| at 8 kHz | A
B
END
angle air supply [°] |  |  | 64.7 | 64.7 | 64.7 | 55.3 | 55.3 | 55.3

## IntermediateCalcul (hidden)
Critical distance
Type | VMV011 | VMV011 | VMV011 | VMV011 | VMV011 | VMV011
Size | 150 | 150 | 150 | 200 | 200 | 200
condition 1 | damper 25% | damper 50% | damper 100% | damper 25% | damper 50% | damper 100%
condition 2
condition 3
A
dT
4
6
8
10
12
B
4
6
8
10
12
dT requested
5
dT1
dT2
A1
A2
B1
B2

## units (hidden)
dB(A)
NR