## SelectionData
Selection Table
flow rate, Q | [m³/h] | 1000
diffuser length | [mm] | 500
diffuser height, H | [mm] | 150 | 50 mm £ H £ 300 mm
throw, LT | [m] | 6 | with ceiling effect
supply temperature, Ts | [°C] | 15
room temperature, Tr | [°C] | 20
room attenuation | [dB(A)] | 8
acoustics unit |  | dB(A)
| Type | Z600 | Z600 | Z600 | Z600 | Z600
| Size | 50 | 100 | 150 | 200 | 250
| condition 1 | 500 mm | 500 mm | 500 mm | 500 mm | 500 mm
condition 2
condition 3
effective air velocity, Veff | [m/s] | 34.4953 | 12.7175 | 7.7958 | 5.6206 | 4.3945
total pressure, DPtot | [Pa] | 594.9622 | 80.8679 | 30.3875 | 15.7958 | 9.6558
throw velocity, vT @ LT | [m/s] | >0.75 | >0.75 | >0.75 | >0.75 | 0.70236
critical distance | [m] | - | - | - | - | -
air temperature @ LT | [°C] | 19.399 | 19.0102 | 18.7357 | 18.5111 | 18.3161
sound power, Lw | [dB(A)] | >55 | >55 | 49.7966 | 44.1895 | 39.8052
sound pressure, Lp | [dB(A)] | >55 | 49.8512 | 41.7966 | 36.1895 | 31.8052
Sound Spectrum
Lw [dB]
125 | [Hz] | - | - | - | - | -
250 | [Hz] | - | - | - | - | -
500 | [Hz] | - | - | - | - | -
1000 | [Hz] | - | - | - | - | -
2000 | [Hz] | - | - | - | - | -
4000 | [Hz] | - | - | - | - | -
8000 | [Hz] | - | - | - | - | -
< BGL : Lw below background level

## units (hidden)
dB(A)
NR

## TechData (hidden)
|  | Type | A600 | A600 | A600 | A600 | A600
|  | Size | 50 | 100 | 150 | 200 | 250
|  | condition 1 | 1000 mm | 1000 mm | 1000 mm | 1000 mm | 1000 mm
condition 2
condition 3
THROW
|  | Ak [m²] | 0.016105 | 0.043684 | 0.071263 | 0.098842 | 0.12642
|  | K1 [m] | 2.9226 | 2.9226 | 2.9226 | 2.9226 | 2.9226
|  | X0 [m] | 0 | 0 | 0 | 0 | 0
PRESSURE LOSS
|  | A | 81.9946 | 222.4037 | 362.8128 | 503.2218 | 643.6309
|  | B | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
total pressure loss |  | Aduct [m²]
CRITICAL DISTANCE (function of DT)
| at 4°C | A
B
| at 6°C | A
B
| at 8°C | A
B
| at 10°C | A
B
| at 12°C | A
B
TEMPERATURE
|  | Ak [m²] | 0.016105 | 0.043684 | 0.071263 | 0.098842 | 0.12642
|  | K2 [-] | 6.081 | 6.081 | 6.081 | 6.081 | 6.081
|  | X0 [m] | 0.075261 | 0.075261 | 0.075261 | 0.075261 | 0.075261
SOUND POWER, NR
|  | A | 20.5317 | 20.4433 | 20.3549 | 20.2665 | 20.1781
|  | B | -84.5421 | -99.595 | -106.9777 | -111.9128 | -115.6252
SOUND POWER, dB(A)
|  | A | 20.5317 | 20.4433 | 20.3549 | 20.2665 | 20.1781
|  | B | -79.5421 | -94.595 | -101.9777 | -106.9128 | -110.6252
SOUND POWER SPECTRUM
| at 125 Hz | A
B
| at 250 Hz | A
B
| at 500 Hz | A
B
| at 1 kHz | A
B
| at 2 kHz | A
B
| at 4 kHz | A
B
| at 8 kHz | A
B
END
angle air supply [°] |  |  | 0 | 0 | 0 | 0 | 0
K1 multiplicative correction factor - no Coanda [-] |  |  | 0.75 | 0.75 | 0.75 | 0.75 | 0.75
correction for angle deflection lamellae
| 15° | Ak [multiplication]
K1 [multiplication]
K2 [multiplication]
Lw [addition]

## IntermediateCalcul (hidden)
Critical distance
Type | A600 | A600 | A600 | A600 | A600
Size | 50 | 100 | 150 | 200 | 250
condition 1 | 1000 mm | 1000 mm | 1000 mm | 1000 mm | 1000 mm
condition 2
condition 3
A
dT
4
6
8
10
12
B
4
6
8
10
12
dT requested
5
dT1
dT2
A1
A2
B1
B2

## CorrectionFactors (hidden)
Noise correction - diffuser length
cNR | -2.9414
Throw correction - diffuser length
cK1 | 0.92285