## SelectionData
Selection Table
flow rate, Q | [m³/h] | 330
throw, LT | [m] | 4
supply temperature, Ts | [°C] | 20
room temperature, Tr | [°C] | 20
room attenuation | [dB(A)] | 8
acoustics unit |  | dB(A)
| Type | CC600 | CC600 | CC600 | CC600 | CC600 | CC600
| Nominal Size | 100 | 125 | 160 | 200 | 250 | 315
| Flow pattern | horizontal | horizontal | horizontal | horizontal | horizontal | horizontal
| Frontplate Position / G [mm] | Pos 3 / +5mm | Pos 3 / +5mm | Pos 3 / +5mm | Pos 3 / +5mm | Pos 3 / +5mm | Pos 3 / +5mm
| Damper position CS001 | 100% (open) | 100% (open) | 100% (open) | 100% (open) | 100% (open) | 100% (open)
duct air velocity, Vduct | [m/s] | 11.6714 | 7.4697 | 4.5591 | 2.9178 | 1.8674 | 1.1763
effective air velocity, Veff | [m/s] | 20.8333 | 13.8889 | 8.3333 | 5.3606 | 3.3951 | 2.1368
static pressure, DPs | [Pa] | 193.9471 | 74.4295 | 21.8997 | 14.3148 | 9.0083 | 5.9778
total pressure, DPtot | [Pa] | 275.6795 | 107.9071 | 34.3711 | 19.4231 | 11.1007 | 6.8079
throw velocity, vT @ LT | [m/s] | 0.33684 | 0.26403 | 0.20911 | 0.20837 | 0.13737 | 0.10931
critical distance | [m] | - | - | - | - | - | -
air temperature @ LT | [°C] | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
sound power, Lw | [dB(A)] | >55 | >55 | 36.0872 | 23.995 | <20 | <20
sound pressure, Lp | [dB(A)] | >55 | 48.954 | 28.0872 | <20 | <20 | <20
Sound Spectrum
Lw [dB]
125 | [Hz] | - | 60.4655 | 46.6371 | 35.7587 | - | -
250 | [Hz] | - | 57.6322 | 39.8635 | 28.3226 | - | -
500 | [Hz] | - | 59.0868 | 33.0286 | 20.2145 | - | -
1000 | [Hz] | - | 54.3822 | 26.1879 | 11.6586 | - | -
2000 | [Hz] | - | 47.3965 | 18.3661 | 2.5702 | - | -
4000 | [Hz] | - | 35.9949 | 7.4505 | < BGL | - | -
8000 | [Hz] | - | < BGL | < BGL | < BGL | - | -
< BGL : Lw below background level

## units (hidden)
dB(A)
NR

## TechData (hidden)
|  | Type | CC600 | CC600 | CC600 | CC600 | CC600 | CC600 | CC600 | CC600 | CC600 | CC600 | CC600 | CC600
|  | Nominal Size | 100 | 125 | 160 | 200 | 250 | 315 | 100 | 125 | 160 | 200 | 250 | 315
|  | Flow pattern | horizontal | horizontal | horizontal | horizontal | horizontal | horizontal | vertical | vertical | vertical | vertical | vertical | vertical
|  | Frontplate Position / G [mm] | Pos 3 / +5mm | Pos 3 / +5mm | Pos 3 / +5mm | Pos 3 / +5mm | Pos 3 / +5mm | Pos 3 / +5mm | 0 | 0 | -5 | -5 | -5 | -5
|  | Damper position CS001 | 100% (open) | 100% (open) | 100% (open) | 100% (open) | 100% (open) | 100% (open) | 100% (open) | 100% (open) | 100% (open) | 100% (open) | 100% (open) | 100% (open)
THROW
|  | Ak [m²] | 0.0044 | 0.0066 | 0.011 | 0.0171 | 0.027 | 0.0429
|  | K1 [m] | 0.975 | 0.936 | 0.957 | 1.189 | 0.985 | 0.988
|  | X0 [m] | 0 | 0 | 0 | 0 | 0 | 0
PRESSURE LOSS
|  | A | 25.3672 | 42.3084 | 71.3892 | 89.1003 | 114.1699 | 137.3216
|  | B | 0.48706 | 0.47661 | 0.49602 | 0.49199 | 0.48286 | 0.49035
|  | Aduct [m²] | 0.007854 | 0.012272 | 0.020106 | 0.031416 | 0.049087 | 0.077931
CRITICAL DISTANCE (function of DT)
| at 4°C | A
B
| at 6°C | A
B
| at 8°C | A
B
| at 10°C | A
B
| at 12°C | A
B
TEMPERATURE
Ak [m²]
K2 [-]
X0 [m]
SOUND POWER, NR
|  | A | 34.904 | 36.3692 | 35.9529 | 36.3327 | 37.7392 | 34.2123
|  | B | -137.6249 | -156.8808 | -178.5333 | -193.1453 | -210.5865 | -196.5057
SOUND POWER, dB(A)
|  | A | 32.5928 | 33.26 | 34.6191 | 34.3105 | 35.7203 | 33.6016
|  | B | -121.2465 | -135.9236 | -164.6723 | -174.9747 | -192.366 | -186.9145
SOUND POWER SPECTRUM
| at 125 Hz | A | 24.2776 | 25.8327 | 29.7651 | 30.5819 | 30.9239 | 30.3617
|  | B | -72.5964 | -89.3406 | -125.9733 | -141.5884 | -151.4459 | -154.4634
| at 250 Hz | A | 30.6557 | 29.0579 | 33.4362 | 33.7894 | 35.0974 | 31.8174
|  | B | -107.8097 | -110.8771 | -154.036 | -167.6251 | -183.8454 | -170.7503
| at 500 Hz | A | 37.977 | 38.4271 | 37.6877 | 35.6667 | 39.8358 | 38.39
|  | B | -148.9728 | -163.7554 | -185.5261 | -186.6198 | -221.5172 | -222.5376
| at 1 kHz | A | 43.6722 | 44.4108 | 43.5074 | 40.9675 | 44.3725 | 42.362
|  | B | -185.1015 | -203.1602 | -226.1159 | -225.9156 | -259.5073 | -256.0002
| at 2 kHz | A | 50.5642 | 48.4106 | 48.4999 | 47.1649 | 50.4937 | 49.2557
|  | B | -228.7631 | -233.3412 | -262.8895 | -270.9435 | -307.468 | -310.1815
| at 4 kHz | A | 49.947 | 47.1288 | 48.1211 | 48.0606 | 51.6968 | 48.9321
|  | B | -234.5555 | -237.3095 | -271.6082 | -287.8125 | -325.9619 | -317.8227
| at 8 kHz | A
B
END

## IntermediateCalcul (hidden)
Critical distance
Type | CC600 | CC600 | CC600 | CC600 | CC600 | CC600 | CC600 | CC600 | CC600 | CC600
Nominal Size | 100 | 125 | 160 | 200 | 250 | 315 | 100 | 125 | 160 | 200
Flow pattern | horizontal | horizontal | horizontal | horizontal | horizontal | horizontal | vertical | vertical | vertical | vertical
Frontplate Position / G [mm] | Pos 3 / +5mm | Pos 3 / +5mm | Pos 3 / +5mm | Pos 3 / +5mm | Pos 3 / +5mm | Pos 3 / +5mm | 0 | 0 | -5 | -5
Damper position CS001 | 100% (open) | 100% (open) | 100% (open) | 100% (open) | 100% (open) | 100% (open) | 100% (open) | 100% (open) | 100% (open) | 100% (open)
A
dT
4
6
8
10
12
B
4
6
8
10
12
dT requested
0
dT1
dT2
A1
A2
B1
B2