## SelectionData
Selection Table
flow rate, Q | [m³/h] | 200
throw, LT | [m] | 4
supply temperature, Ts | [°C] | 20
room temperature, Tr | [°C] | 20
room attenuation | [dB(A)] | 8
acoustics unit |  | dB(A)
| Type | CS400 | CS400 | CS400 | CS400 | CS400 | CS400 | CS400 | CS400 | CS400 | CS400 | CS400 | CS400
| Nominal Size | 100 | 125 | 160 | 200 | 250 | 315 | 100 | 125 | 160 | 200 | 250 | 315
| Flow pattern | horizontal | horizontal | horizontal | horizontal | horizontal | horizontal | vertical | vertical | vertical | vertical | vertical | vertical
| Frontplate Position / G [mm] | Pos 3 / +5mm | Pos 3 / +5mm | Pos 3 / +5mm | Pos 3 / +5mm | Pos 3 / +5mm | Pos 3 / +5mm | Pos 4 / +0mm | Pos 4 / +0mm | Pos 5 / -5mm | Pos 5 / -5mm | Pos 5 / -5mm | Pos 5 / -5mm
| Damper position CS001 | 100% (open) | 100% (open) | 100% (open) | 100% (open) | 100% (open) | 100% (open) | 100% (open) | 100% (open) | 100% (open) | 100% (open) | 100% (open) | 100% (open)
duct air velocity, Vduct | [m/s] | 7.0736 | 4.5271 | 2.7631 | 1.7684 | 1.1318 | 0.71288 | 7.0736 | 4.5271 | 2.7631 | 1.7684 | 1.1318 | 0.71288
effective air velocity, Veff | [m/s] | 10.3867 | 6.8868 | 4.2086 | 3.032 | 2.3902 | 2.0684 | 12.7319 | 7.9556 | 4.9386 | 3.834 | 3.0611 | 2.5303
static pressure, DPs | [Pa] | 44.3487 | 26.2606 | 7.7223 | 4.6396 | 3.1213 | 2.3366 | 64.4787 | 40.0787 | 13.941 | 9.6002 | 6.894 | 5.0984
total pressure, DPtot | [Pa] | 74.3698 | 38.5572 | 12.3032 | 6.516 | 3.8898 | 2.6415 | 94.4998 | 52.3753 | 18.5219 | 11.4766 | 7.6626 | 5.4033
throw velocity, vT @ LT | [m/s] | 0.15226 | 0.13834 | 0.1113 | 0.083797 | 0.08085 | 0.063407 | 0.26028 | 0.20556 | 0.17559 | 0.1449 | 0.12907 | 0.11903
critical distance | [m] | - | - | - | - | - | - | - | - | - | - | - | -
air temperature @ LT | [°C] | - | - | - | - | - | - | - | - | - | - | - | -
sound power, Lw | [dB(A)] | >55 | 41.6819 | <20 | <20 | <20 | <20 | 53.9656 | 43.0182 | 27.0693 | 21.0702 | <20 | <20
sound pressure, Lp | [dB(A)] | 50.0852 | 33.6819 | <20 | <20 | <20 | <20 | 45.9656 | 35.0182 | <20 | <20 | <20 | <20
Sound Spectrum
|  | Lw [dB] | [5 empty] | Lw [dB]
125 | [Hz] | 65.3529 | 52.3706 | - | - | - | - | 62.7816 | 55.1052 | 40.5354 | 35.9235 | - | -
250 | [Hz] | 61.6125 | 46.4394 | - | - | - | - | 54.6215 | 45.2908 | 29.8565 | 21.6404 | - | -
500 | [Hz] | 57.4003 | 37.9794 | - | - | - | - | 52.3994 | 39.4655 | 20.801 | 13.5361 | - | -
1000 | [Hz] | 52.2951 | 30.3964 | - | - | - | - | 49.0357 | 33.764 | 14.4516 | 7.9888 | - | -
2000 | [Hz] | 51.1706 | 25.5233 | - | - | - | - | 45.552 | 29.8337 | 4.0646 | < BGL | - | -
4000 | [Hz] | < BGL | < BGL | - | - | - | - | < BGL | < BGL | < BGL | < BGL | - | -
8000 | [Hz] | < BGL | < BGL | - | - | - | - | < BGL | < BGL | < BGL | < BGL | - | -
< BGL : Lw below background level

## units (hidden)
dB(A)
NR

## TechData (hidden)
|  | Type | CS400 | CS400 | CS400 | CS400 | CS400 | CS400 | CS400 | CS400 | CS400 | CS400 | CS400 | CS400
|  | Nominal Size | 100 | 125 | 160 | 200 | 250 | 315 | 100 | 125 | 160 | 200 | 250 | 315
|  | Flow pattern | horizontal | horizontal | horizontal | horizontal | horizontal | horizontal | vertical | vertical | vertical | vertical | vertical | vertical
|  | Frontplate Position / G [mm] | Pos 3 / +5mm | Pos 3 / +5mm | Pos 3 / +5mm | Pos 3 / +5mm | Pos 3 / +5mm | Pos 3 / +5mm | Pos 4 / +0mm | Pos 4 / +0mm | Pos 5 / -5mm | Pos 5 / -5mm | Pos 5 / -5mm | Pos 5 / -5mm
|  | Damper position CS001 | 100% (open) | 100% (open) | 100% (open) | 100% (open) | 100% (open) | 100% (open) | 100% (open) | 100% (open) | 100% (open) | 100% (open) | 100% (open) | 100% (open)
THROW
|  | Ak [m²] | 0.0053487 | 0.008067 | 0.0132 | 0.018323 | 0.023244 | 0.026859 | 0.0043635 | 0.0069832 | 0.011249 | 0.01449 | 0.018149 | 0.021956
|  | K1 [m] | 0.79094 | 0.88653 | 0.92887 | 0.78261 | 0.84872 | 0.69961 | 1.2379 | 1.2368 | 1.3409 | 1.2558 | 1.2519 | 1.2699
|  | X0 [m] | 0.053954 | 0.03607 | -0.035305 | 0.16692 | 0.17477 | 0.25974 | 0 | 0 | 0 | 0 | 0 | 0
PRESSURE LOSS
|  | A | 32.3833 | 44.8113 | 78.0885 | 98.3509 | 117.5278 | 131.0888 | 25.3347 | 32.1551 | 53.5249 | 60.754 | 72.8751 | 83.0819
|  | B | 0.48013 | 0.45772 | 0.46009 | 0.4625 | 0.46708 | 0.49775 | 0.49591 | 0.49521 | 0.50029 | 0.52679 | 0.52292 | 0.5393
|  | Aduct [m²] | 0.007854 | 0.012272 | 0.020106 | 0.031416 | 0.049087 | 0.077931 | 0.007854 | 0.012272 | 0.020106 | 0.031416 | 0.049087 | 0.077931
CRITICAL DISTANCE (function of DT)
| at 4°C | A
B
| at 6°C | A
B
| at 8°C | A
B
| at 10°C | A
B
| at 12°C | A
B
TEMPERATURE
Ak [m²]
K2 [-]
X0 [m]
SOUND POWER, NR
|  | A | 36.8532 | 34.9882 | 34.8855 | 34.6528 | 35.2741 | 33.7947 | 30.4997 | 29.8534 | 29.1021 | 25.8381 | 31.7623 | 31.3551
|  | B | -141.9131 | -148.5815 | -172.5032 | -181.9082 | -196.6228 | -195.1772 | -113.375 | -120.6976 | -132.8882 | -121.0367 | -165.5134 | -168.5133
SOUND POWER, dB(A)
|  | A | 34.9216 | 32.5843 | 33.1605 | 32.5884 | 32.9514 | 31.0412 | 29.4533 | 30.3394 | 28.9986 | 26.3186 | 29.9472 | 28.5242
|  | B | -126.9405 | -130.9599 | -155.9527 | -163.0914 | -174.8205 | -170.2296 | -102.0874 | -117.7294 | -126.5745 | -118.3741 | -147.7479 | -144.278
SOUND POWER SPECTRUM
| at 125 Hz | A | 29.5974 | 27.1307 | 29.8323 | 30.148 | 30.8394 | 29.5479 | 26.9566 | 33.4928 | 24.7747 | 21.9071 | 27.6332 | 27.3919
|  | B | -91.4635 | -91.3766 | -125.2142 | -136.2601 | -150.0457 | -148.7949 | -80.043 | -122.3504 | -90.729 | -80.1475 | -121.9967 | -125.3332
| at 250 Hz | A | 34.2735 | 35.4122 | 33.2113 | 32.3509 | 31.4929 | 30.0316 | 26.0442 | 25.0298 | 30.676 | 30.0785 | 29.8857 | 27.6815
|  | B | -119.9792 | -141.1857 | -152.9997 | -158.8008 | -162.9158 | -160.7511 | -83.3689 | -87.3252 | -132.6746 | -137.7248 | -144.6672 | -136.0025
| at 500 Hz | A | 38.9941 | 37.9858 | 35.0103 | 34.0193 | 33.54 | 31.0803 | 31.0606 | 32.3263 | 33.4119 | 30.6184 | 31.3932 | 29.785
|  | B | -149.2028 | -163.2813 | -170.8183 | -176.3401 | -182.6819 | -174.5842 | -112.1697 | -131.8097 | -156.2258 | -148.6902 | -160.8038 | -156.6669
| at 1 kHz | A | 42.051 | 38.4853 | 37.9942 | 36.306 | 36.3621 | 34.406 | 36.1142 | 34.8895 | 35.8591 | 31.6168 | 31.8862 | 31.7463
|  | B | -170.5042 | -173.5111 | -192.6715 | -194.4103 | -204.1173 | -200.6182 | -142.3087 | -151.0919 | -175.5413 | -159.5267 | -167.6912 | -173.5335
| at 2 kHz | A | 51.1491 | 40.7129 | 41.2052 | 42.3425 | 41.4443 | 38.4267 | 38.3432 | 37.9603 | 43.795 | 36.2166 | 37.2687 | 29.462
|  | B | -219.8335 | -190.1864 | -218.6569 | -238.6151 | -243.7603 | -234.5459 | -157.6027 | -171.292 | -227.9754 | -193.3702 | -207.5393 | -164.3398
| at 4 kHz | A
B
| at 8 kHz | A
B
END

## IntermediateCalcul (hidden)
Critical distance
Type | CS400 | CS400 | CS400 | CS400 | CS400 | CS400 | CS400 | CS400 | CS400 | CS400
Nominal Size | 100 | 125 | 160 | 200 | 250 | 315 | 100 | 125 | 160 | 200
Flow pattern | horizontal | horizontal | horizontal | horizontal | horizontal | horizontal | vertical | vertical | vertical | vertical
Frontplate Position / G [mm] | Pos 3 / +5mm | Pos 3 / +5mm | Pos 3 / +5mm | Pos 3 / +5mm | Pos 3 / +5mm | Pos 3 / +5mm | Pos 4 / +0mm | Pos 4 / +0mm | Pos 5 / -5mm | Pos 5 / -5mm
Damper position CS001 | 100% (open) | 100% (open) | 100% (open) | 100% (open) | 100% (open) | 100% (open) | 100% (open) | 100% (open) | 100% (open) | 100% (open)
A
dT
4
6
8
10
12
B
4
6
8
10
12
dT requested
0
dT1
dT2
A1
A2
B1
B2